## Sheet1
Photovoltaic system dimensioning
Simplified spreadsheet for photovoltaic calculations
Solar radiation data for a given site available from:
https://eosweb.larc.nasa.gov/sse/RETScreen/ , Worldwide coverage
http://globalsolaratlas.info/ , Worldwide coverage
http://re.jrc.ec.europa.eu/pvgis/apps4/pvest.php?map=africa&lang=en, Africa and Eurasia coverage
Input data framed in red |  |  | Intermediate results framed in blue |  | Final results framed in green
Device | Consumption,W | Hours/day | Energy/day, Wh
Electrical Load Calculation
GPS | 1.5 | 24 | 36
WiFi Client | 8 | 24 | 192
Laptop | 15 | 12 | 180
WiFi AP | 3 | 24 | 72
Ethernet Switch | 4 | 24 | 96
Total energy consumption/day, Wh |  |  | 36
Battery capacity calculation, considering the number of no-sun days and the allowed depth of discharge
Required autonomy, days |  | Depth of Discharge |  | Battery capacity,Wh | Battery voltage,V | Battery Capacity, Ah | Number of batteries
4 |  | 0.5 |  | 288 | 12 | 24 | 2
Panel capacity calculation |  | Panel Peak power, Wp
10
Load energy,Wh | Battery charging allowance |  | Energy /d, Wh | PSH | Daily Photovoltaic power, W |  | Number of panels
36 | 1.5 |  | 54 | 5.5 | 9.8182 |  | 1
Stationary batteries should not be discharged more tha 50%, automotive batteries no more than 20%
Battery charging allowance to partially charge the battery bank after the estimated number of no-sun days has ocurred
Solar radiation in kWh/day per square meter is numerically equal to the number of Peak Sun Hours (PSH) per day
Keep in mind that there are considerable uncertainties in the insolation and no-sun days estimates, so caution is required